[bookmark: _GoBack]   Electric Meter Safety – Meter Socket Verification
[image: ]Before energizing a new or upgraded service, a meter socket verification test should be performed. This will identify a possible back-feed situation or fault before it happens. Donn the appropriate PPE to perform the verification test.
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Single-Phase, Three-Wire
For 240/480V services, double the voltage readings in these checks.

Check 1. Line-side voltage
Ato B=240 volts
120 volts

Check 2. Backfeed

ato Neutral = 0 volts

b to Neutral volts

Voltage reading other than 0 indicates backfeed
from the load side. Do not continue until condition
is corrected.

Check 3. Load-side fault
Atoa=0volts

Btob=0volts

Voltage reading other than 0 indicates a fault from
atoN, orbto . Do not set meter until condition is
corected

Add temporary jumper - Neutral to b

Atob=120volts
Checks the jumper connections before proceeding.

Atoa=0volts
Vohage reading other than 0 indicates a fault from a
tob. Do not et meter until condition i corrected.

Remove jumper.




