                      Electric Meter Safety

When removing or installing an electric meter under load, an arc can be created, the meter could short out causing an explosion or the meter glass could break; all of which could cause serious injury or death.
The best practice to follow when removing or installing a single phase self-contained electric meter from or into the meter socket, is to shut off the main breaker at the main panel in house.  If a bypass (horn type or lever) is available at the meter socket, this shall be used if the main breaker cannot be shut off.
A meter puller shall be used (to remove and install the meter) in the event that the main breaker cannot be turned off. The meter puller will help prevent injury from an explosion, breaking glass or an arc flash. Low voltage class 0 or 00 gloves, hard hat, safety glasses, possibly a face shield and FR clothing must also be worn.
[bookmark: _GoBack]Note: Cooperative in house policy (such as: No single phase electric meter shall be removed or installed under load. The main breaker must be shut off) may supersede the language above. 
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