THIS IS AN EXAMPLE OF HOW TO FILL OUT THE INFORMATION SHARING CHECKLIST!
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	The Host must ensure that the contractor(s), subcontractors and all employees are provided information on the following:
 I. CHARACTERISTICS OF HOST EMPLOYER'S INSTALLATION RELATED TO SAFETY (REQUIRED):

	1. The nominal voltages of lines and equipment
	 
	7.2 / 12.5 KV  Distribution; 69KV Sub-transmission (69KV substation only)
	 
	 

	2. Maximum switching-transient voltages
	X
	 
	 
	 

	3. The presence of hazardous induced voltages
	 
	In vicinity of poles 12475-12477 exists a crossing 345KV Transmission Line. 
	 
	 

	4. The presence and condition of protective grounds and equipment grounding conductors
	 
	No personal grounds installed on system by host unless notified by host. Equipment grounding conductors are in place as is typical on a wye system.
	 
	 

	5. The locations of circuits and equipment, including electric supply lines, communication lines and fire-protective signaling circuits
	 
	See computer-based mapping system.
	 
	 

	II. Conditions that are related to safety (if info is available in existing records):

	6. Condition of the protective grounds and equipment grounding conductors
	 
	Unknown
	 
	 

	7. Condition of the poles
	 
	All poles in the area were tested 3 years ago. All poles determined to be deteriorated at that time have been replaced; See note below concerning field testing of structures.
	 
	 

	8. Environmental conditions relating to safety
	 
	Unknown
	 
	 

	III. INFORMATION ABOUT THE DESIGN AND OPERATION OF HOST EMPLOYER'S INSTALLATION NEEDED TO MAKE ASSESSMENTS
Assessment required by contractor:                                                       Type of information to be provided by host employer:

	Whether an enclosed space must be entered as a permit-required confined space.
	Whether an enclosed space contains hazards, other than electrical and atmospheric hazards, that could endanger the life of an entrant or could interfere with escape from the space.
	X
	 
	 
	 

	Whether forced air ventilation has been maintained long enough that a safe atmosphere exists.
	The size of the enclosed space.
	X
	 
	 
	 

	What is the minimum approach distance for the work to be performed?
	What the operating conditions are for the value of the maximum transient overvoltage provided to the contract employer.
	 
	MAD should be determined using voltages stated under "characteristics", and transient over-voltages do not apply.
	 
	 

	Whether employees are exposed to hazards from flames or electric arcs.
	Information on electric equipment, such as safety information provided by manufacturers, that relates to the required hazard assessment.
	 
	Versa-Tech reclosers made by Hubbell are on the system. Unlike conventional reclosers, the tanks are energized rather than grounded; Hot Line Tag features on the electronic recloser control at the substation will lockout the recloser faster than conventional non-reclosing settings. 
	 
	 

	What is the estimated incident energy from an electric arc?
	The electrical parameters needed to calculate incident energy, such as maximum fault current, buss spacings, and clearing times.
	 
	Maximum fault current of 5,000 amps; 15 cycle clearing time with normal reclosing disabled. 
	 
	 

	Whether protective grounds have adequate current-carrying capacity.
	The maximum fault current and clearing time for the circuit.
	 
	Maximum fault current of 5,000 amps with a 15 cycle clearing time when normal reclosing is disabled. 
	 
	 

	Whether devices are designed to open or close circuits under load conditions.
	Load current for, and the opening and closing ratings of, devices used to open and close circuits under load.
	 
	All reclosing devices are designed to be opened and closed under load conditions. GH type sectionalizers on the system are also designed to be opened and closed under load, but incapable of being closed under fault current conditions. All fused cutouts absent of load-break features are not made to break load without use of a load-break tool. 
	 
	 

	What are the known sources of electric energy (including known sources of back-feed) supplying electric circuits?
	All known sources of electric energy, including known sources of back-feed.
	 
	NOVA triple-single protecting Feeder #2 at Oak Substation with 69KV high side feed using solid material high-side fuses. Open point feeding from Feeder 3 of Elm Substation shall continue as an open point. Distributed generation biomass site at 2160 No-Man’s Road. All meters must be assumed to be capable of producing back-feed through portable generators.
	 
	 

	Whether there is a possibility of hazardous transfer of potential should a fault occur.
	Potential rise on remote grounds under fault conditions.
	 
	A hazardous transfer of potential can occur during the event of a fault if any part of the system's multi-grounded neutral is opened even at a remote location on the distribution system, even with personal protective grounds installed. 
	 
	 

	Whether overhead structures such as poles and towers are capable of sustaining stresses imposed by the work.
	The design strength of the pole or structure.
	 
	As written in the work order, all structures are of sufficient strength to carry the stresses, however, all structures must always be field tested using industry standard practices before placing additional strain on or changing the stresses on the structure.
	 
	 

	IV. Other known system information related to safety and requested by contractor:

 
 
	 
	 

	 Signature of Employer Representative                                   Date
 
	Signature of Contractor Representative                                   Date






This sample is provided for informational purposes only and should not be relied on as legal advice. The sample cannot and does not address the unique facts and circumstances of your specific situation and should not be relied on for your particular transaction. QSI, Inc. makes no claims, promises, or guarantees about the accuracy, completeness, or adequacy of any information contained in the samples. Therefore, you should not use the sample without first obtaining the advice of your business attorney. Finally, nothing contained in this sample should be construed to constitute a recommendation or endorsement of QSI, Inc. 
